# Standard Operating Procedure (SOP)

## Startup, Operation & Shutdown of Centrifugal Pump P-101

### Document Information

| Field | Value |
| --- | --- |
| Document ID | SOP-OPS-P101-002 |
| Equipment Tag | P-101 |
| Department | Operations |
| Revision | 1.0 |
| Effective Date | 15 July 2026 |
| Prepared By | Operations Department |
| Approved By | Operations Manager |

# 1. Purpose

This Standard Operating Procedure (SOP) defines the correct method for starting, operating, monitoring, and shutting down Centrifugal Pump P-101 to ensure safe, efficient, and reliable process operation.

# 2. Scope

This SOP applies to all operators responsible for operating Pump P-101 in the Process Water Transfer System.

# 3. Responsibilities

### Shift Operator

- Perform pre-startup inspections.

- Monitor pump performance during operation.

- Report abnormalities immediately.

### Shift Supervisor

- Authorize startup after maintenance.

- Review operating logs.

- Ensure compliance with safety procedures.

# 4. Safety Requirements

Before operating the pump:

- Wear required PPE.

- Verify work permits are closed.

- Ensure no Lockout/Tagout (LOTO) tags remain.

- Confirm maintenance work has been completed.

- Ensure all guards are installed.

- Verify emergency stop is functional.

# 5. Operating Parameters

| Parameter | Normal Range |
| --- | --- |
| Flow Rate | 110–120 m³/hr |
| Discharge Pressure | 3.5–4.0 bar |
| Suction Pressure | 1.2–1.5 bar |
| Motor Current | 22–25 A |
| Bearing Temperature | < 80°C |
| Motor Temperature | < 85°C |
| Vibration | < 4.5 mm/s |

# 6. Pre-Startup Checklist

Verify the following:

☐ Pump casing is filled with liquid.

☐ Suction valve fully open.

☐ Discharge valve partially open.

☐ Motor power available.

☐ No abnormal leakage.

☐ Lubrication completed.

☐ Cooling water available (if applicable).

☐ Mechanical seal flushed.

☐ Pressure gauges operational.

☐ Area is clean and free of obstructions.

# 7. Startup Procedure

- Inform the control room.

- Verify process line is ready.

- Open suction valve completely.

- Crack open discharge valve approximately 25%.

- Prime the pump if required.

- Start the motor from the control panel.

- Observe motor current.

- Gradually open the discharge valve to operating position.

- Verify discharge pressure.

- Check for unusual vibration or noise.

- Record startup time in the logbook.

# 8. Normal Operation

During operation, monitor every 30 minutes:

- Flow rate

- Suction pressure

- Discharge pressure

- Motor current

- Bearing temperature

- Seal leakage

- Pump vibration

- Noise level

Report any abnormal readings to the Shift Supervisor.

# 9. Alarm Conditions

| Alarm | Operator Action |
| --- | --- |
| High vibration | Reduce load and inspect alignment. |
| High bearing temperature | Notify maintenance immediately. |
| Low discharge pressure | Check suction line and impeller condition. |
| Excessive seal leakage | Prepare standby pump and inform maintenance. |
| High motor current | Reduce flow and inspect for blockage. |

# 10. Emergency Shutdown

Immediately stop Pump P-101 if any of the following occurs:

- Motor trips.

- Bearing temperature exceeds 90°C.

- Fire in pump area.

- Major seal failure.

- Severe vibration.

- Pump casing rupture.

- Electrical fault.

- Loss of suction causing continuous cavitation.

Notify the Control Room immediately after shutdown.

# 11. Normal Shutdown Procedure

- Inform the control room.

- Gradually close the discharge valve.

- Stop the motor.

- Close the suction valve if extended shutdown is planned.

- Drain the pump if maintenance is required.

- Record shutdown time.

- Inspect for leaks.

# 12. Abnormal Conditions

### Pump Not Delivering Flow

Possible causes:

- Air lock

- Closed suction valve

- Empty suction tank

- Worn impeller

Corrective action:

- Stop the pump.

- Identify root cause.

- Restart only after issue is resolved.

### Excessive Vibration

Possible causes:

- Misalignment

- Bearing damage

- Cavitation

- Loose foundation bolts

Corrective action:

- Reduce load.

- Notify Maintenance Department.

- Switch to standby pump if vibration exceeds limits.

### Seal Leakage

Small leakage is acceptable.

Continuous or heavy leakage requires maintenance intervention.

# 13. Operating Log Sheet

| Time | Flow | Suction Pressure | Discharge Pressure | Motor Current | Bearing Temp | Remarks |
| --- | --- | --- | --- | --- | --- | --- |

# 14. Environmental Precautions

- Prevent water spills.

- Report leaks immediately.

- Dispose of contaminated absorbents according to plant procedures.

- Ensure drainage systems remain unobstructed.

# 15. References

- Maintenance Manual MM-P101-001

- Plant Safety Manual

- Lockout/Tagout Procedure

- Preventive Maintenance Schedule

- Emergency Response Procedure

# 16. Revision History

| Revision | Date | Description |
| --- | --- | --- |
| 1.0 | 15-Jul-2026 | Initial issue |